## Sheet1
Point | Addresses inside GUI | Modbus-addresses | Physical Address (PLC) | Remarque
//boilerPressureControl
BPC_BOILER_CURR_PRESSURE | 4101 | 44102 | D5
BPC_CONDENSER_CURR_PRESSURE | 4171 | 44172 | D75
BPC_SET_ATMOSPHERIC_VALVE_OPENING | 1284 | 1285 | Y4
BPC_OPEN_OR_AUTOMATIC_ATMOSPHERIC_VALVE | 2059 | 2060 | M11
BPC_AUTOMAN_SETPOINT_PRESSURE | 2060 | 2061 | M12
BPC_SETPOINT_ATMOSPHERIC_PRESSURE | 4105 | 44106 | D9
//turbineGoveringSystem
TGS_CURR_TURBINE_SPEED | 4107 | 44108 | D11
TGS_CURR_VALVE_OPENING | 4128 | 44129 | D32
TGS_SET_VALVE_OPENING | 4109 | 44110 | D13
TGS_AUTOMAN_VALVE | 2068 | 2069 | M20
TGS_AUTOMAN_SETPOINT_RPM | 2069 | 2070 | M21
TGS_SETPOINT_RPM | 4106 | 44107 | D10
//inceneratorPowerControl
IPC_SET_SUPPLYFAN | 1300 | 1301 | Y4, Ext
IPC_CURR_SUPPLYFAN_STATUS | 1044 | 11045 | X4, Ext
IPC_SET_FUELBURNER1 | 1302 | 1303 | Y6,EXT
IPC_CURR_FUELBURNER1_STATUS | 1046 | 11047 | X6,EXT
IPC_SET_EXHAUSTFAN1 | 1296 | 1297 | Y0, Ext
IPC_CURR_EXHAUSTFAN1_STATUS | 1040 | 11041 | X0, Ext
IPC_SET_EXHAUSTFAN2 | 1281 | 1282 | Y1
IPC_CURR_EXHAUSTFAN2_STATUS | 1025 | 11026 | X1
IPC_SET_Water_COOLINGPUMP | 1298 | 1299 | Y2, Ext
IPC_CURR_Water_COOLINGPUMP_STATUS | 1042 | 11043 | X2, Ext
//FilteringSystem
FS_SET_ELECTROFILTER | 1297 | 1298 | Y1, Ext
FS_CURR_ELECTROFILTER_STATUS | 1041 | 11042 | X1,EXT
FS_CURR_TEMPERATURE1_incinerator | 4146 | 44147 | D50
FS_CURR_TEMPERATURE_After_Chemical_FILTER | 8208 | 8209 | Temperature Controller
FS_CURR_TEMPERATURE_After_Cooling | 5208 | 45209 | D1112
FS_SET_Chemical_PUMP | 1282 | 1283 | Y2
FS_CURR_Chemical_PUMP_STATUS | 1026 | 11027 | X2
FS_SET_Air_COOLINGPUMP | 1303 | 1304 | Y7, Ext
FS_CURR_Air_COOLINGPUMP_STATUS | 1047 | 11048 | X7, Ext
//Boiler Level Control
LC_CURR_LEVELCONTROL_STATUS | 1030 | 11031 | X6
LC_SET_WATER STEAM CYCLE MAIN PUMP 3PHASE | 1301 | 1302 | Y5, Ext
LC_CURR_WATER STEAM CYCLE MAIN PUMP 3PHASEE_STATUS | 1045 | 11046 | X5, Ext
LC_SET_WATER PUMP 1PHASE | 1299 | 1300 | Y3, Ext
LC_CURR_WATER PUMP 1PHASE | 1043 | 11044 | X3, Ext
Coil/Register Numbers | Data Addresses | Type | Table Name
1 to 9999 |  | Read-Write | Discrete Output Coils
10001-19999 | 0000 to 270E | Read-Only | Discrete Input Contacts
30001-39999 | 0000 to 270E | Read-Only | Analog Input Registers
40001-49999 | 0000 to 270E | Read-Write | Analog Output Holding Registers